PART F - INDIVIDUAL TREATMENT SPECIFICATION

| TREATMENT/ACTIVITY NAME | Power Poles/Lines Replacement | PART E BIA Spec-# | 3_Power Poles/Lines Replacement |
| --- | --- | --- | --- |
| NFPORS TREATMENT CATEGORY* | Facility & Infrastructure | FISCAL YEAR(S) (list each year): | 2008 |
| NFPORS TREATMENT TYPE * | Water System Reconstruction | WUI? Y / N | Y |
| IMPACTED COMMUNITIES AT RISK | Rincon Tribal Residents | IMPACTED T&E SPECIES | NA |

* See NFPORS Restoration & Rehabilitation module - Edit Treatment screen for applicable entries.

WORK TO BE DONE (describe or attach exact specifications of work to be done):

A. General Description: Replace two fire-damaged power poles and associated lines and other infrastructure to restore power for normal domestic water delivery to Tribal residents. The poles and lines are owned, operated, and maintained by BIA. B. Location/(Suitable) Sites: The damaged structures and lines described above are on the Rincon Reservation. They are located on West Tribal road that leads to the softball field and former tribal office. (see attached maps) C. Design/Construction Specifications: For required safety clearance between lines, SDG&E raises its existing West Tribal Road power line at least 4 feet (Contact: Fred Purkiss @ 760-445-1793 or 760-480-7644 0r Brian Swanson @ 858-967-7121) Install one angle/transformer wooden pole Install 2-8 foot cross-arms for insulators, 2-10 foot cross-arms for transformers attachment, and 1-8 foot cross-arm for cutouts. Install 3-12 KV cutouts, 3-100 Amp fuses, 3-cutouts, and associated hardware. Transfer 3 existing transformers to the new pole, transfer 4 kV conductors, and re-tie and install new conductors for the line. (It is estimated up to 50 ft of new wire may be needed) Replace 1-3/8” guy wire support. Install one single wooden pole structure, cross-arm, and associated hardware. D. Purpose of Treatment Specifications (relate to damage/change caused by fire): To restore normal power supply to the pump station that enables domestic water delivery to tribal residents. E. Treatment consistent with Agency Land Management Plan (identify which plan): Southern California Agency Fire Management Plan (FIREWISE 2000) with approved EA and signed FONSI; also refer to 1914 Contract between United States and the Escondido Mutual Water Company. F. Treatment Effectiveness Monitoring Proposed: Completion of treatment (repair job) to be verified by Implementation Leader.

LABOR, MATERIALS AND OTHER COST:

| PERSONNEL SERVICES: (Grade @ Cost/Hours X # Hours X # Fiscal Years = Cost/Item): Do not include contract personnel costs here (see contractor services below). | COST / ITEM |
| --- | --- |
| TOTAL PERSONNEL SERVICE COST |  |
| EQUIPMENT PURCHASE, LEASE AND/OR RENT (Item @ Cost/Hour X # of Hours X #Fiscal Years = Cost/Item): Note: Purchases require written justification that demonstrates cost benefits over leasing or renting. |  |
| TOTAL EQUIPMENT PURCHASE, LEASE OR RENTAL COST |  |
| MATERIALS AND SUPPLIES (Item @ Cost/Each X Quantity X #Fiscal Years = Cost/Item): |  |
| TOTAL MATERIALS AND SUPPLY COST |  |
| TRAVEL COST (Personnel or Equipment @ Rate X Round Trips X #Fiscal Years = Cost/Item): |  |
| TOTAL TRAVEL COST |  |
| CONTRACT COST (Labor or Equipment @ Cost/Hour X #Hours X #Fiscal Years = Cost/Item): |  |
| Lump sum-fixed rate commercial contract (1 repair job @ $14,700 X 1 fiscal year = $14,700): Remove and install 1-35’ angle/transformer pole Install 2-8 foot cross-arms Install 2-10 foot cross-arms. Install 1-8 foot cross-arm. Install 3-12 kV cutouts, 3-100 Amp fuses, and associated hardware. Transfer 3 existing transformers to new poles, 4 kV conductors, re-tie and install new conductors. Replace 1 – 3/8” guy wire support. Install 1 – 35’ single pole, including cross-arm, insulators, and associated hardware. | $6,000.00 $350.00 $350.00 $200.00 $600.00 $2000.00 $200.00 $5,000.00 |
| TOTAL CONTRACT COST | $14,700.00 |

| SPECIFICATION COST SUMMARY |
| --- |
| FISCAL YEAR | PLANNED INITIATION DATE (M/D/YYYY) | PLANNED COMPLETION DATE (M/D/YYYY) | WORK AGENT | UNITS | UNIT COST | PLANNED ACCOMPLISHMENTS | PLANNED COST |
| 2008 | 11/20/2007 | 11/30/2007 | S | Job | 14,700 | 1 | $14,700 |
| TOTAL | $14,700 |

Work Agent: C=Coop Agreement, F=Force Account, G=Grantee, P=Permittees, S=Service Contract, T=Timber Sales Purchaser, V=Volunteer

SOURCE OF COST ESTIMATE

| 1. Estimate obtained from 2-3 independent contractual sources. |  |
| --- | --- |
| 2. Documented cost figures from similar project work obtained from local agency sources. | C |
| 3. Estimate supported by cost guides from independent sources or other federal agencies |  |
| 4. Estimates based upon government wage rates and material cost. |  |
| 5. No cost estimate required - cost charged to Fire Suppression Account |  |

P = Personnel Services,   E = Equipment   M = Materials/Supplies,   T = Travel,   C = Contract,   F = Suppression

RELEVANT DETAILS, MAPS AND DOCUMENTATION INCLUDED IN THIS REPORT:

See Public Safety and Facilities Assessment, Appendix I; see attached maps depicting power line alignment location and damaged line area and pole replacement locations; see Watershed Treatment Map, Appendix 4.

TOTAL COST BY JURSIDICTION

| TRIBAL JURISDICTION | Poomacha | Harris | Witch | UNITS TREATED | COST |
| --- | --- | --- | --- | --- | --- |
| Rincon | $14,700 |  |  | 1 | $14,700 |
| TOTAL COST |  |  |  |  | $14,700 |